## Sheet1
Code	Desc	Value	Applicable Constant Mode	Notes		Hold “SET” and “UP arrow” together, enter password set values with “SET” Key, Save changes with RST Key
F0	Temperature Setting	21.5		21.5(F0)+3(F2)= 24.5 Target temp
F1	Temperature difference values	x	NO
F2	Cooling Hysteresis	3
F3	Way of Control	0
F4	Alarm for over high water Temp	4.5		21 (F0) + 4.5 (F4)= 25.5= Alarm E2
F5	Alarm for over low water Temp	7.5		21 (F0) – 7.5 (F5)= 13.5 = Alarm
F6	Alarm for over high room temp	40
F7	Password	8
F8	The highest allowed water temp	25.5
F9	The lowest allowed water temp	13.5